Copyright 2017 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Stored Energy Systems, LLC ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA). Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Stored Energy Systems, LLC, 1840 Industrial Circle, Longmont, CO 80501; Phone: (303) 678-7500; Fax: (303) 678-7504; Website: sens-usa.com; Email: info@sens-usa.com.

For information about MasterSpec, contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 263343 – BATTERY CHARGERS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes: Battery chargers for use with standby and emergency engine generators.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

ACTION SUBMITTALS

Product Data: For each type of battery charger.

Include system overview, construction details, material descriptions, and dimensions of battery charging and monitoring systems.

Include rated capacities, operating characteristics, electrical characteristics, performance specifications, and furnished accessories.

Shop Drawings: For battery chargers.

Include plans, elevations, sections, and mounting details.

Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field installation, components, and location and size of each field connection.

Include diagrams for power, signal, and control wiring.

Include instructions for installer.

INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For manufacturer.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

Seismic Qualification Certificates: For battery changers, accessories, and components, from manufacturer.

Basis for Certification: Include Certificate of Compliance for nonstructural components and systems. Withstand certification is for below grade, grade, and roof-level installations, installations in essential facilities, and for life safety applications, based on actual shake-testing. Certified installation locations shall include mounting directly to structural wall and directly to non-structural wall.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

Manufacturer's operating specifications and user's guides.

Data sheet for each battery charger with nameplate information and performance specifications.

QUALITY ASSURANCE

Manufacturer Qualifications: Provide certification that manufacturer meets the requirements of ISO 9001.

WARRANTY

When warranties longer than one year are required and would exceed the "one-year period for correction of Work," verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Manufacturer's Warranty: Manufacturer agrees to repair or replace components of battery chargers that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components.

Warranty Period: Three years from date of sale to original purchaser.

Special Warranty: Extended warranty to either five (5) or ten (10) years from date of original shipment.

Warranties specified in Division 01 Specification Sections shall be in addition to, and run concurrent with, other warranties required by the Contract Documents. Manufacturer's disclaimers and limitations on product warranties do not relieve Contractor of obligations under requirements of the Contract Documents.

Contractor covers period from date of sale to date of substantial completion.

PRODUCTS

PERFORMANCE REQUIREMENTS

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

UL Compliance: Comply with UL 1236 for category BBHH. OEM-supplied open-frame chargers may be UL recognized to BBHH provided they are housed in a listed enclosure.

NFPA Compliance: Comply with NFPA 110.

Environmental Conditions: Battery charger shall withstand the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

Ambient Temperature: Minus 40 to plus 158 deg F (minus 40 to plus 70 deg C) with full charger output available up to 104 deg F (40 deg C).

Relative Humidity: 5 to 95 percent.

Altitude: Meets full performance from sea level to 5000 feet (1600 m). Chargers installed at higher altitudes may automatically derate output power to prevent overheating of internal components, but shall remain operable.

Electromagnetic Immunity: Charger power terminals shall be immune to conducted and radiated electromagnetic energy to EN 61000-4-12.

Vibration Resistance: Charger enclosure rated to EN 60068-2-6; 4G, 18 to 500 Hz on 3 axes, and random 20 to 500 Hz, 0.01 G2 per Hz.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

Seismic Performance: Battery chargers shall withstand the effects of earthquake motions determined according to [IBC 2006] [IBC 2009] [IBC 2012] [IBC 2015] [the latest edition of the IBC] [ASCE/SEI 7] <Insert requirement>.

Shake-Table Testing: Comply with ICC-ES AC156.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as standby and emergency engine generators), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

Component Importance Factor, Ip:  1.5.

Short-Period Design Spectral Acceleration, SDS, Equipment at Grade (z/h = 0.0): 2.50 g.

Short-Period Design Spectral Acceleration, SDS, Equipment on Roof (z/h = 1.0): 2.00 g.

Battery Charger Power Conversion Energy Efficiency:

Certified to California Code of Regulations, Title 20, Appliance Efficiency Regulations, https://cacertappliances.energy.ca.gov/Pages/ApplianceSearch.aspx.

Comply with Oregon Department of Energy standards for appliance energy efficiency.

BATTERY CHARGERS FOR EMERGENCY ENGINE GENERATORS

The majority of emergency engine generator (genset) starting failures are due to dead starting batteries. When failing, genset batteries frequently fail catastrophically and sometimes explosively. Vehicle starting batteries, in contrast, last about twice as long as genset starting batteries and almost never fail catastrophically. This is despite the fact that the exact same type of flooded starting, lighting, and ignition (SLI) batteries are used in gensets and vehicles. Battery chargers in this Section emulate how vehicle batteries are charged in the "Lead-Acid Battery Longevity and Safety Mode". The battery charger operates continuously, but with reduced charging voltage to cut the rate of separator oxidation. The charger periodically operates at a higher charging voltage to ensure that the battery remains charged and ready.

Manufacturers and products listed in SpecAgent and MasterWorks Paragraph Builder are neither recommended nor endorsed by the AIA or ARCOM. Before inserting names, verify that manufacturers and products listed there comply with requirements retained or revised in descriptions and are both available and suitable for the intended applications. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

Basis-of-Design Product: Subject to compliance with requirements, provide Stored Energy Systems, LLC; MicroGenius family [MicroGenius2] [MicroGenius2e] [MicroGeniusS2] [MicroGeniusS4] or a comparable product by one of the following:

<Insert manufacturer's name>.

Battery Charger Operation: Current-limited, constant voltage, automatic-boost type charger designed for [lead-acid] [nickel-cadmium] batteries, with the following features:

Automatic Boost Mode: Operates in boost charging mode after battery discharge. Boost duration automatically adjusted depending on the following:

Differing depths of battery discharge.

Differing relationships of battery amp-hour capacity to charger ampere output.

Differing parasitic direct current loads.

Output Voltage Regulation: Charger regulates output to within plus or minus 0.5 percent of manufacturer-provided voltage settings despite variations of input voltage, input frequency, and output current.

Battery Thermal Compensation: Battery temperature compensation with adjustable slope, factory set at minus 0.18 percent per degree C, and equipped for sensing battery temperature. [Include battery temperature sensor mounted on battery negative terminal.]

Automatic Dead Battery Recharge: Charger automatically recharges a battery discharged to zero volts at full rated output current, without the need for user intervention.

AC Input: Charger operates from any 47 to 63 Hz alternating-current-source with voltage ranging from 90 to 265 V rms.

Lead-Acid Battery Longevity and Safety Mode: Charger emulates vehicle duty for which starting batteries are designed to maximize battery life, minimize battery explosion risk, and minimize electrolyte loss in lead-acid batteries:

Boost Mode Recharge: After recharge is complete in boost mode, charger reverts to a voltage just above battery open circuit voltage, for the majority of battery charger operating hours, when fully charged. The charger remains in operational to prevent battery discharge.

Float Mode: Charger periodically elevates output voltage to insure a fully charged battery, charger then returns to just above battery nominal voltage. Charger repeats this this cycle until the next battery discharge, when the battery shall be recharged in the boost mode.

Charger Enclosure: NEMA 250, [Type 1 (IP20)] [Type 3R (IP22)], wall-mounted and rated for generator duty with charger enclosure vibration resistance. Housing materials: aluminum or stainless steel.

Battery Charger Status Indication and Alarms:

If the battery charger is conveying voltage, current, and alarm data via J-1939 data link, confirm that generator control panel is capable of displaying voltage, current, and alarm information. Otherwise, employ meters on the battery charger, and Form C contacts, to convey this data.

Output Voltage and Current: Digital or analog meters on front panel, or by conveying performance data to generator control panel via J-1939 data link. Accuracy: Plus 2 percent for voltage and plus 5 percent for current.

Alarm Outputs: [Individual Form C contacts] [Single summary Form C contact], or by conveying alarms to generator control panel via J-1939 data link:

AC voltage failure.

Low DC voltage.

High DC voltage.

Low cranking voltage.

SOURCE QUALITY CONTROL

Retain "Testing Agency" Paragraph below if required. Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

Testing Agency: [Owner will engage] [Engage] a qualified testing agency to evaluate battery charger fabricator's quality-control and testing methods.

Testing: Test and inspect battery chargers according to UL 1236 for BBHH recharge performance.

Retain "Factory Tests" Paragraph below for factory-assembled battery chargers. Factory tests are an added cost option and may not be available from some manufacturers. Verify requirement with Owner.

Factory Tests: Test and inspect assembled battery chargers to manufacturer's published specifications. Verify NFPA 110 recharge performance by validating that battery charger is listed to UL category BBHH on the UL certification database.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Battery charger will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

EXECUTION

EXAMINATION

Examine areas, mounting locations, and conditions, with Installer present, for compliance with requirements for installation and other conditions affecting battery charger performance.

Examine roughing-in for conduit systems and electrical connections. Verify actual locations of connections before battery charger installation.

Proceed with installation only after unsatisfactory conditions have been corrected.

BATTERY CHARGER INSTALLATION

Follow manufacturer's instructions to prevent damage from static electricity. Provide clearances for service and ventilation.

Battery chargers are configured at the factory. If settings need to be field-configured, follow manufacturer's setup instructions.

Coordinate jumper data links with emergency generator control panel capabilities.

CONNECTIONS

Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables." Provide branch circuit overcurrent protection.

Comply with requirements for branch circuit protection and service disconnects in Section 262816 "Enclosed Switches and Circuit Breakers."

IDENTIFICATION

Identify system components according to Section 260553 "Identification for Electrical Systems."

FIELD QUALITY CONTROL

Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain the following tests and inspections paragraph below to require Contractor to perform tests and inspections, or to perform tests and inspections witnessed by authorities having jurisdiction.

Perform the following tests and inspections[ with the authority having jurisdiction] [ with the assistance of a factory-authorized service representative]:

Verify that certification labels are properly installed. Verify NFPA 110 compliance by validating that battery charger is listed to UL category BBHH on the UL certification database.

Verify that connections are secure and in the proper locations. Ensure wiring is correctly connected between charger and battery.

Operational Test: After electrical circuitry has been energized, apply input voltage to confirm proper unit operation.

Test and adjust alarms, display indicators, controls, and safeties.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Battery charger will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain battery chargers and related equipment.

Coordinate this training with that for emergency engine generator equipment.

END OF SECTION 263343